Analysis of the Tugela-Vaal Bridging Proposal

A K Bailey1 & J R Hansford2

1Stewart Scott, P.O. Box 784506, Sandton, 2146.

2Knight Piésold, P.O. Box 221, Rivonia, 2128

Introduction

The Tugela Basin already makes a significant contribution to the water supply of the Gauteng province.  The Drakensberg pumped storage scheme currently transfers on average about 20 m3/s to the Vaal system and another 1,5 m3/s comes in from Zaaihoek Dam in the Slang River to supply Majuba power station.  The Department of Water Affairs and Forestry (DWAF) has commissioned extensive studies to seek the best means of augmenting supplies by up to 40 m3/s.  One of the studies involves extending the existing transfer of water from the Tugela basin and is referred to as the Vaal Augmentation Planning Study:  Tugela-Vaal Transfer Scheme (TVTS).  Meanwhile a major scheme for transfer of up to 8 m3/s from the Tugela to the Mhlatuze River is already at design stage.  The entire Tugela Basin is thus being analysed with the envisaged maximum transfer rate of around 70 m3/s, which is equivalent to more than half its average annual natural runoff.

Phase 1a of the Lesotho Highlands scheme has been delayed one to two years as a result of the need to line the tunnel and so is not expected to come on stream before 1999 or 2000.  Severe drought over the past few years has left current storage levels in the Vaal supply system disturbingly low.  Operational analyses of the system show that unless augmentation from Lesotho can start in 1998, as originally planned, the risk of shortfall in the Vaal system will become unacceptably high.  At the minimum level of supply the shortfall during 1998 is estimated at between 200 and 300 x 106 m3.  DWAF has therefore commissioned a study of the so-called bridging scheme, involving examination of the merits of increasing the transfer of water by way of the existing Drakensberg pumped storage scheme.  Although the projected shortfalls in supply to Gauteng relate to the year 1998, DWAF's initial request was for the additional transfer to be accomplished by the end of 1999.  The WST consortium comprising the consulting firms Knight Piesold, Stewart Scott and Consultburo, formed to undertake the TVTS study, was appointed for the investigation.

The Drakensberg scheme currently involves diversion of up to 4 m3/s from run-of-river in the upper Tugela and pumping of up to 19 m3/s from Driel barrage into a canal leading to Jagersrust.  River regulation is by means of storage in Woodstock Dam, located in the Tugela upstream of the barrage.  From Jagersrust reservoir the water is pumped to Kilburn Dam, the tailwater pond of the pumped storage hydro scheme.  Analyses by Eskom's engineers have indicated that the maximum average rate of transfer to the Vaal system can be increased from the present 20 m3/s to 35 m3/s without adversely affecting the flexibility of the scheme from the power generation point of view.  As even the current transfer is not firm, it follows that to increase the transfer rate would require additional resources.  Spioenkop Dam, being under-utilised at present, offers potential for transfer.  Demands on Spioenkop Dam, averaging only 23 x 106 m3/annum, are those of Ladysmith, Colenso and irrigation.  Historical releases of 83,3 x 106 m3/annum, however, average almost four times the demand.  No significant growth in demand on Spioenkop Dam between now and the end of the century is envisaged.

Three proposals for increasing the transfer to the Vaal utilising the surplus at Spioenkop Dam and the potential at the Drakensberg hydro scheme were assessed, namely:

●	An emergency scheme, envisaging short-term over-abstraction or "mining" of Spioenkop Dam.

●	A conjunctive scheme, involving continuous pumping from Spioenkop Dam into the transfer canal from Driel with supply from Driel regulated so that flow in the canals is maintained at their full capacities.

●	A backup scheme, involving augmentation of the supply at Driel by pumping from Spioenkop Dam when shortfalls occur.

The paper describes simulated operation of the systems with the aid of the Water Resources Yield Model (WRYM) so that the benefits of each of the three proposals can be assessed and compared.

The Physical System

A map of the area (see Figure 1) shows the Woodstock, Kilburn and Spioenkop Dams, the Driel Barrage, the Jagersrust and Driel pumping stations and the canal network.  The Tugela River system was modelled as far downstream as Colenso.  The capacities of the canals and pumping stations are shown on Figure 1.  The Tuva canal from Driel to the confluence with the upper Tugela canal from Putterill can readily be upgraded from a capacity of 19 m3/s to 21 m3/s.  From the confluence to Jagersrust pumping station and onwards to Kilburn Dam, the capacity of the carrier is 23 m3/s.  The upper Tugela canal and the Driel -Jagersrust canal seldom flow at full capacity.  Augmentation from other sources are required to achieve a continuous flow of 23 m3/s.

Hydrological time series and water demands were taken from the reports of the TVTS reconnaissance study.  For easy reference these data are summarised in Tables 1 and 2.  Water demands projected to 1998 were used throughout the analyses.

Table 1: Sub-catchment inflow

| WRYM Incremental inflow datafile | Description | Mean Annual Runoff (106 m3/a) |
| --- | --- | --- |
| TM01 | Upstream of the Putterill diversion | 74.32 |
| TM02 | Downstream of the Putterill diversion and upstream of Woodstock Dam | 362.84 |
| TM03 | Local inflow to Woodstock Dam and Driel Barrage | 22.27 |
| TM04 | Mlambonja River | 217.84 |
| TM05 | Downstream of Driel Barrage and upstream of Spioenkop Dam | 88.43 |
| TM06 | Farm dams upstream of Spioenkop Dam | 31.07 |
| TM07 | Downstream of Spioenkop Dam | 16.00 |
| TM08 | Little Tugela River | 309.35 |

Table 2: Details of mean annual abstractions

| Demand Name (Refer to Figure 2) | Description of demand | Demand (106 m3/a) |
| --- | --- | --- |
| THWOOD.IRD | Irrigation upstream of Woodstock Dam | 5.00 |
| TM02.IRD | Irrigation from farm dams upstream of Woodstock | 2.23 |
| THDRIEL.IRD | Irrigation upstream of Driel Barrage (Mlambonja River) | 2.35 |
| THSKOP.IRD | Irrigation upstream of Spioenkop Dam | 44.89 |
| TM06.IRD | Irrigation from farm dams upstream of Spioenkop Dam | 11.13 |
| THSKOPDS.IRD | Irrigation downstream of Spioenkop Dam | 4.01 |
| THLTUG.IRD | Irrigation from the Little Tugela River | 30.60 |
| V1R001.MD | Urban demand from Spioenkop Dam for Ladysmith | 7.88 |
| COLENSO.MD | Urban demand for Colenso | 0.63 |

Modelling the System

Analysis was with the aid of WRYM which requires that the system be described as a network of nodes and channels.  Although the program allows for many different channel types, they all fall into either of two categories, namely: flow channels of which the carrying capacities are split into discrete ranges, with a penalty (or cost) assigned to the flow in each range, and demand channels having penalties imposed for failure to meet the specified demand (or flow).  Nodes can be either reservoir nodes or junction nodes.  Reservoir nodes are points in the system where there is storage and natural flow, possibly also inflows or outflows.  Junction nodes need not have natural inflow but have no storage and are used merely to interconnect channels.  Reservoir storage is subdivided into layers called zones.  Each zone is assigned a penalty to represent the cost (or value) of the water in the zone.  A "rule curve" is associated with each reservoir in the system.  Water stored below the level defined by the rule curve has a value but water stored above the rule curve is stored at a cost to the system.  All penalties assigned to flow into, out of or through the various components are relative.  However, although the penalties have no real meaning, WRYM operates the system to minimise the total penalties for each iteration.  Thus the penalties serve to define the operating rules and priorities within the system.  There is no unique solution for a workable set of penalties and the onus is on the user to select appropriate relative penalties to ensure that the system will operate as envisaged.

The system network diagram in Figure 2 shows the upper reaches of the Tugela catchment.  The reservoirs were modelled using four zones.  The rule curve was set to the bottom of the top zone with the penalty set high so that water would not be stored above full supply level.  The bottom zone, below dead storage level, was also assigned a high penalty so that the model would not attempt to take water from this zone to meet demands.  The two intermediate working storage zones in all except Spioenkop Dam were assigned the same penalty so that they would in effect operate as one zone.  In Spioenkop Dam, the lower zone was assigned a higher penalty so that water in this zone could be reserved for downstream demands and not used for transfer.

WRYM is a monthly model.  Monthly flows, however, are not uniform and therefore uniform abstractions from run-of-river or from small volumes of storage cannot necessarily be fully met even though average inflow may have exceeded demand.  This condition applies to the Putterill diversion as well as to pumping from Driel Barrage.  At Putterill, the diversion channel (see channel 1 in Figure 2) was such that only a percentage of the inflow at the node could be diverted.  Driel Barrage has about 10x106m3 of storage, compared with the monthly abstraction of about 50x106m3.  The major inflow to Driel is from the Mlambonja River which joins the Tugela just upstream of the barrage.  The daily flow record in the Mlambonja was used to estimate how much of the Mlambonja flow could be pumped each month from the limited storage at Driel into the transfer canal.  This estimate was used to set the parameters for a diversion channel (see channel 38 in Figure 2) that would bypass part (often most) of the flow of the Mlambonja around Driel to the downstream node, thus reducing the likelihood of overestimating the yield at Driel.

The demand channel penalties were set so that Tugela basin demands would be met in preference to transfer demands.  By simply changing the penalty value in the abstraction channels from Driel and Spioenkop respectively, the scheme could be changed from the conjunctive proposal to the backup proposal (see channels 27 and 28 in Figure 2).  For the emergency proposal, one additional change was made in that the abstraction from Spioenkop Dam was not linked to the other existing transfers but simply taken to a point outside the system.  The transfer channel limits and penalties used to simulate operation of the three proposals are shown in Figure 2.

System Analysis

The three proposals and the existing Drakensberg scheme were analysed using 201 five-year-long stochastic inflow sequences to simulate possible operations during the five years January 1995 to December 1999, with the starting storages in the reservoirs set to the recorded levels as at 6 January 1995.  The results of the simulations were stored in the WRYM output datafile (.PLT) and subsequently analysed with the aid of post-processors to identify the  benefit of each of the proposals.  Details are outlined in the following sections.

Emergency supply from Spioenkop

The emergency proposal was analysed to assess the volume of water that could be transferred between January and December 1999 at a maximum transfer rate of 7 m3/s (see channel 28 in Figure 2).  This would depend on the volume of water in Spioenkop Dam at the beginning of 1999.  Accordingly, operation of the existing scheme was simulated from January 1995 with the emergency transfer introduced in January 1999.  The advantage of this proposal was that a decision to implement could be made later than for the other proposals.  This would be offset to an extent, however,  by the additional cost of installing a large conveyance to transfer of the order of 7 m3/s all the way from Spioenkop to Kilburn.

Conjunctive use of Spioenkop supply

The conjunctive use proposal envisages a canal of capacity either 2 or 4 m3/s to deliver water from Spioenkop Dam into the transfer canal at Driel.  The proposal was operated in such a way that water would be supplied continuously from Spioenkop, subject to available resources, with transfers from Driel used to regulate flow so that maximum carrier capacities were not exceeded.  Operation of the system was simulated from January 1995 with starting conditions as recorded and with Spioenkop supply introduced in January 1997.

Backup supply from Spioenkop Dam

The backup proposal was operated so that water would be supplied from Spioenkop only when supply from Putterill and Driel left spare capacity in the canals.  This proposal was analysed using the same 2 m3/s and 4 m3/s canal capacities as before and with the scheme also introduced in January 1997.

The backup system was re-analysed without introducing the supply from Spioenkop so that the monthly transfer rates from the existing scheme could be determined.  These monthly transfer flow rates were accumulated using a post-processor to calculate the volume transferred by the existing scheme during each of the 201 sequences.  The results were ranked and plotted as shown in Figure 3.  It is important to note that, for a specific level of assurance, the additional volumes demanded for the three schemes, as well as for the existing system, were not necessarily from the same sequence.  It would therefore be wrong to add the volume yielded by the existing scheme to that of one of the three proposed schemes and regard that as the volume that could be transferred at this level of assurance.

The same post-processor was used to manipulate the results from the transfer proposal simulations.  The net benefit of each proposal was calculated by subtracting the volumes transferred by the existing scheme from the total transferred for each sequence.  The net transfer volumes were ranked and plotted as shown in Figure 4.  Table 3 summarises the results for the existing scheme and for the three bridging proposals.

Table 3 : Summary of bridging scheme analysis results

| Assurance (%) | RI | Existing scheme Total volume (106m3) January 1995 to December 1999 | Conjunctive use system Additional volume (106m3) |  | Backup system Additional volume (106m3) |  | Emergency scheme. Additional volume transferred during 1999 (106m3) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | January 1997 to December 1999 |  |  |  |  |
|  |  |  | Link capacity from Spioenkop |  |  |  |  |
|  |  |  | 2.0 m3/s | 4.0 m3/s | 2.0 m3/s | 4.0 m3/s | 7.0 m3/s |
| 99.5 | 1:200 | 2 358 | 147 | 211 | 140 | 141 | 172 |
| 99.0 | 1:100 | 2 378 | 148 | 214 | 141 | 142 | 173 |
| 98.0 | 1:50 | 2 462 | 149 | 221 | 143 | 143 | 174 |
| 95.0 | 1:20 | 2 494 | 153 | 228 | 147 | 147 | 182 |
| 90.0 | 1:10 | 2 593 | 156 | 241 | 150 | 153 | 191 |
| 80.0 | 1:5 | 2 702 | 164 | 250 | 157 | 165 | 211 |
| 50.0 | 1:2 | 2 934 | 175 | 282 | 165 | 192 | 221 |

Conclusions

The results show that the conjunctive use proposal with the 4 m3/s conveyance from Spioenkop Dam would be the most beneficial from the point of view of volume of water transferred.  As stated in the introduction, shortfall of 200 to 300 x 106m3 can be expected in 1998.  The volume of water that the conjunctive use proposal can be expected to deliver by the end of 1999, at a 99.5% level of assurance would exceed the lower estimate by only about 5%.  Clearly by the end of 1998 the volume transferred would be significantly less.  This together with other factors not covered in this paper led to abandonment of the bridging proposal.

Acknowledgements

The authors thank the Director-General, Department of Water Affairs and Forestry, for permission to publish the paper and Professor DC Midgley for his valuable comments.

Table 3 : Summary of bridging scheme analysis results

| Assurance (%) | RI | Existing scheme Total volume (106m3) January 1995 to December 1999 | Conjunctive use system Additional volume (106m3) |  | Backup system Additional volume (106m3) |  | Emergency scheme. Additional volume transferred during 1999 (106m3) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | January 1977 to December 1999 |  |  |  |  |
|  |  |  | Link capacity from Spioenkop |  |  |  |  |
|  |  |  | 2.0 m3/s | 4.0 m3/s | 2.0 m3/s | 4.0 m3/s | 7.0 m3/s |
| 99.5 | 1:200 | 2 358 | 147 | 211 | 140 | 141 | 172 |
| 99.0 | 1:100 | 2 378 | 148 | 214 | 141 | 142 | 173 |
| 98.0 | 1:50 | 2 462 | 149 | 221 | 143 | 143 | 174 |
| 95.0 | 1:20 | 2 494 | 153 | 228 | 147 | 147 | 182 |
| 90.0 | 1:10 | 2 593 | 156 | 241 | 150 | 153 | 191 |
| 80.0 | 1:5 | 2 702 | 164 | 250 | 157 | 165 | 211 |
| 50.0 | 1:2 | 2 934 | 175 | 282 | 165 | 192 | 221 |